## Uvals
Heat loss from a building
Area | 1565.0824 | m2 | (ground floor area)
U Values
|  | U value | Comment
| Wall | 0.2795 | See calc | (below)
| Window | 2.2 | CIBSE Table
| Floor | 0.23789
| Roof | 0.3337
| Doors | 2.2 | Table
Walls | [5 empty] | Walls
| Layer | Thickness | k value | Resistance |  |  | Layer | Thickness | k value | Resistance
| Outer |  |  | 0.06 |  |  | Outer |  |  | 0.06
| Outer brick | 100 | 0.84 | 0.11905 |  |  | Outer brick | 100 | 0.84 | 0.11905
| Air gap | 50 |  | 0.18 |  |  | Air gap
| Insulation | 100 | 0.04 | 2.5 |  |  | Insulation | 100 | 0.035 | 2.8571
| Inner brick | 100 | 0.19 | 0.52632 |  |  | Inner brick | 100 | 0.19 | 0.52632
| Plaster | 10 | 0.16 | 0.0625 |  |  | Plaster |  |  | 0
| Inner |  |  | 0.13 |  |  | Inner |  |  | 0.12
|  |  | Sum | 3.5779 |  |  |  |  | Sum | 3.6825
|  |  | U value | 0.2795 |  |  |  |  | U value | 0.27155
Roof
| Layer | Thickness | k value | Resistance
| Outer surface |  |  | 0.04
| Felt layers | 10 | 0.5 | 0.02
| Air gap | 50 |  | 0.18
| Insulation | 100 | 0.04 | 2.5
| Timber | 25 | 0.14 | 0.17857
| Plasterboard | 12.5 | 0.16 | 0.078125
| Inner surface |  |  | 0.1
|  |  | Sum | 2.9967 | =sum R
|  |  | U value | 0.3337 | =1/sum R
Floor
| Building Perimeter | 43
| Building Area | 114
| P/A | 0.37719
| c1 | 0.05 | c2 | 1.65 | c3 | -0.6
| U value | 0.587 | R | 1.7036
|  | Thickness | k value | Resistance
| Insulation | 100 | 0.04 | 2.5
|  |  | Sum | 4.2036
|  |  | U value (tot) | 0.23789

## Room_01
Building
Room Ref | L | W | Hint | Afloor(m2) | Vroom (m3)
Classroom | 12.5 | 6 | 3 | 75 | 225
Classroom | 12.5 | 6 | 3 | 75 | 225
Classroom | 12.5 | 6 | 3 | 75 | 225
PC Lab | 12.5 | 6 | 3 | 75 | 225
PC Lab | 12.5 | 6 | 3 | 75 | 225
Stair 1 | 13 | 2.5 | 3 | 16.25 | 48.75
Stair 2 | 3 | 7.5 | 3 | 22.5 | 67.5
Threater | 13.5 | 13.5 | 3 | 143.1388 | 429.4164
Tutorial Classroom | 11 | 11 | 3 | 63.3555 | 190.0664
Tutorial Classroom | 11 | 11 | 3 | 63.3555 | 190.0664
Tutorial Classroom | 11 | 11 | 3 | 63.3555 | 190.0664
Tutorial Classroom | 11 | 11 | 3 | 63.3555 | 190.0664
Tutorial Classroom | 11 | 11 | 3 | 63.3555 | 190.0664
Tutorial Classroom | 11 | 11 | 3 | 63.3555 | 190.0664
Café | 22.5 | 29.5 | 3 | 331.875 | 995.625
Toilet | 16 | 8.5 | 3 | 68 | 204
Corridor1 | 25 | 3 | 3 | 75 | 225
Corridor2 | 27.5 | 3 | 3 | 82.5 | 247.5
Corridor3 | 27.5 | 3 | 3 | 70.6858 | 212.0575
|  |  | Totals | 1565.0824 | 4695.2471

## Ht Loss_house1
Heat loss from a building （Original） | [22 empty] | Source
Area | 1565.0824 | m2 | PSR | 1.2 | PSR/E | 1.2 |  | Qloss |  |  | 82377.0535 | W | Qloss/Af | 52.6343 | W/m2 |  |  |  |  | Q_solar | 44885.25 | kW | PVGIS
N | 1 | h-1 | Eff Fac | 1 |  |  |  | Qhtg |  |  | 98852.4642 | W | Qhtg/Af | 63.1612 | W/m2 |  |  |  |  | E_solar | 26931.15 | kWh/yr
Tao | -3 | deg C | [5 empty] | Ndd |  |  | 2360
|  |  | PSR = plant size ratio |  |  |  |  | Ehtg |  |  | 202862.4483 | kWh | DT | 23 | E/A | 129.6177 | kWh/m2/yr
U values
(used in Building Part L) |  |  | Comment
| Walls | 0.2795 | See calc
| Windows | 2.2 | CIBSE Table
| Floors | 0.45
| Roofs | 0.45
| Doors | 2.2
Room | Wall |  | Window |  | Floor |  | Ceiling |  | Door |  | Wall |  | Window |  | Floor |  | Ceiling |  | Doors |  | sum | Infiltration | Tai | Tao | Tai-Tao | Sum(UA)+nV/3 | Heat Loss | Heat Loss Rate(%) | Heat Loss | Heat loss
| Length | Height | Length | Height | Length | Width | Length | Width | Length | Width | U value | UA | U value | UA | U value | UA | U value | UA | U value | UA | UA | nV/3 | [6 empty] | per unit Area | x factor
| (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) |  | (WK-1) | (oC) | (oC) | (oC) | (WK-1) | (W) |  | (W/m2) | (W)
Classroom (70 seats)_ | 11 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 1.8 | 2 | 0.2795 | 9.2234 | 2.2 | 0 | 0.45 | 33.75 | 0.45 | 33.75 | 2.2 | 7.92 | 84.6434 | 75 | 20 | -3 | 23 | 159.6434 | 3671.7978 | 4.4573 | 48.9573 | 4406.1573 | 4.4573
Classroom (70 seats)_ | 6 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 1.8 | 2 | 0.2795 | 5.0309 | 2.2 | 0 | 0.45 | 33.75 | 0.45 | 33.75 | 2.2 | 7.92 | 80.4509 | 75 | 20 | -3 | 23 | 155.4509 | 3575.3715 | 4.3403 | 47.6716 | 4290.4458 | 4.3403
Classroom (70 seats)_ | 6 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 1.8 | 2 | 0.2795 | 5.0309 | 2.2 | 0 | 0.45 | 33.75 | 0.45 | 33.75 | 2.2 | 7.92 | 80.4509 | 75 | 20 | -3 | 23 | 155.4509 | 3575.3715 | 4.3403 | 47.6716 | 4290.4458 | 4.3403
PC Lab (20 pcs) | 6 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 0.9 | 2 | 0.2795 | 5.0309 | 2.2 | 0 | 0.45 | 33.75 | 0.45 | 33.75 | 2.2 | 3.96 | 76.4909 | 75 | 20 | -3 | 23 | 151.4909 | 3484.2915 | 4.2297 | 46.4572 | 4181.1498 | 4.2297
PC Lab (20 pcs) | 11 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 0.9 | 2 | 0.2795 | 9.2234 | 2.2 | 0 | 0.45 | 33.75 | 0.45 | 33.75 | 2.2 | 3.96 | 80.6834 | 75 | 20 | -3 | 23 | 155.6834 | 3580.7178 | 4.3467 | 47.7429 | 4296.8613 | 4.3467
Stair 1 | 10 | 3 | 10 | 2.5 | 13 | 2.5 | 9 | 2.5 | 1.8 | 2 | 0.2795 | 1.3975 | 2.2 | 55 | 0.45 | 7.3125 | 0.45 | 5.0625 | 2.2 | 7.92 | 76.6925 | 32.5 | 20 | -3 | 23 | 109.1925 | 2511.4271 | 3.0487 | 77.2747 | 3013.7125 | 3.0487
Stair 2 | 10.5 | 3 | 0 | 0 | 3 | 7.5 | 3 | 7.5 | 0.9 | 2 | 0.2795 | 8.8041 | 2.2 | 0 | 0.45 | 7.3125 | 0.45 | 10.125 | 2.2 | 3.96 | 30.2016 | 16.25 | 20 | -3 | 23 | 46.4516 | 1068.3877 | 1.2969 | 47.4839 | 1282.0652 | 1.2969
Threater (150 seats) | 0 | 3 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.5 | 3.6 | 2 | 0.2795 | 0 | 2.2 | 0 | 0.45 | 64.4125 | 0.45 | 64.4125 | 2.2 | 15.84 | 144.6649 | 143.1388 | 20 | -3 | 23 | 287.8037 | 6619.4862 | 8.0356 | 36.3209 | 7943.3835 | 8.0356
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.2795 | 1.1455 | 2.2 | 38.5 | 0.45 | 28.51 | 0.45 | 28.51 | 2.2 | 7.92 | 104.5854 | 63.3555 | 20 | -3 | 23 | 167.9409 | 3862.6398 | 4.689 | 31.9226 | 4635.1677 | 4.689
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.2795 | 1.1455 | 2.2 | 38.5 | 0.45 | 28.51 | 0.45 | 28.51 | 2.2 | 7.92 | 104.5854 | 63.3555 | 20 | -3 | 23 | 167.9409 | 3862.6398 | 4.689 | 31.9226 | 4635.1677 | 4.689
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.2795 | 1.1455 | 2.2 | 38.5 | 0.45 | 28.51 | 0.45 | 28.51 | 2.2 | 7.92 | 104.5854 | 63.3555 | 20 | -3 | 23 | 167.9409 | 3862.6398 | 4.689 | 31.9226 | 4635.1677 | 4.689
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.2795 | 1.1455 | 2.2 | 38.5 | 0.45 | 28.51 | 0.45 | 28.51 | 2.2 | 7.92 | 104.5854 | 63.3555 | 20 | -3 | 23 | 167.9409 | 3862.6398 | 4.689 | 31.9226 | 4635.1677 | 4.689
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.2795 | 1.1455 | 2.2 | 38.5 | 0.45 | 28.51 | 0.45 | 28.51 | 2.2 | 7.92 | 104.5854 | 63.3555 | 20 | -3 | 23 | 167.9409 | 3862.6398 | 4.689 | 31.9226 | 4635.1677 | 4.689
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.2795 | 1.1455 | 2.2 | 38.5 | 0.45 | 28.51 | 0.45 | 28.51 | 2.2 | 7.92 | 104.5854 | 63.3555 | 20 | -3 | 23 | 167.9409 | 3862.6398 | 4.689 | 31.9226 | 4635.1677 | 4.689
Café (24 seats) | 42.7 | 3 | 29 | 2.5 | 22.5 | 29.5 | 22.5 | 29.5 | 10.5 | 2 | 0.2795 | 15.54 | 2.2 | 159.5 | 0.45 | 149.3438 | 0.45 | 149.3438 | 2.2 | 46.2 | 519.9275 | 331.875 | 20 | -3 | 23 | 851.8025 | 19591.4575 | 23.7827 | 29.5163 | 23509.749 | 23.7827
Toilet | 9 | 3 | 9 | 2.5 | 16 | 8.5 | 16 | 8.5 | 2.7 | 2 | 0.2795 | 1.2577 | 2.2 | 49.5 | 0.45 | 30.6 | 0.45 | 30.6 | 2.2 | 11.88 | 123.8377 | 68 | 20 | -3 | 23 | 191.8377 | 4412.2679 | 5.3562 | 32.4431 | 5294.7215 | 5.3562
Corridor1 | 6 | 3 | 0 | 0 | 25 | 3 | 25 | 3 | 3.6 | 2 | 0.2795 | 5.0309 | 2.2 | 0 | 0.45 | 33.75 | 0.45 | 33.75 | 2.2 | 15.84 | 88.3709 | 75 | 20 | -3 | 23 | 163.3709 | 3757.5315 | 4.5614 | 50.1004 | 4509.0378 | 4.5614
Corridor2 | 0 | 0 | 0 | 0 | 27.5 | 3 | 27.5 | 3 | 1.8 | 2 | 0.2795 | 0 | 2.2 | 0 | 0.45 | 37.125 | 0.45 | 37.125 | 2.2 | 7.92 | 82.17 | 0 | 20 | -3 | 23 | 82.17 | 1889.91 | 2.2942 | 22.908 | 2267.892 | 2.2942
Corridor3 | 0 | 0 | 0 | 0 | 27.5 | 3 | 27.5 | 3 | 0 | 0 | 0.2795 | 0 | 2.2 | 0 | 0.45 | 31.8086 | 0.45 | 31.8086 | 2.2 | 0 | 63.6173 | 0 | 20 | -3 | 23 | 63.6173 | 1463.1968 | 1.7762 | 17.7357 | 1755.8361 | 1.7762
[26 empty] | Total Heat Loss | 82377.0535 |  | 52.6343 | 98852.4642
|  | Floor |  |  | Floor Area (m2)
|  | stair 1 |  |  | 16.25
|  | stair 2 |  |  | 22.5
|  | Threater |  |  | 143.1388
|  | Tutorial Classroom |  |  | 63.3555
|  | café |  |  | 331.875
|  | Toilet |  |  | 68
|  | Corridor3 |  |  | 70.6858
|  | PC |  |  | 75
|  | Corridor2 |  |  | 82.5
|  | Corridor1 |  |  | 75

## Ht Loss_house2
Heat loss from a building （Improved） | [22 empty] | Source
Area | 1565.0824 | m2 | PSR | 1.2 | PSR/E | 1.2 |  | Qloss |  |  | 27141.2883 | W | Qloss/Af | 17.3418 | W/m2 |  |  |  |  | Q_solar | 128338.5 | kW | PVGIS
N | 0.15 | h-1 | Eff Fac | 1 |  |  |  | Qhtg |  |  | 32569.546 | W | Qhtg/Af | 20.8101 | W/m2 |  |  |  | Window | E_solar | 77003.1 | kWh/yr
Tao | -3 | deg C | [5 empty] | Ndd |  |  | 2200 | [7 empty] | roof | E_solar | 23100.93
|  |  | PSR = plant size ratio |  |  |  |  | Ehtg |  |  | 62306.9575 | kWh | DT | 23 | E/A | 39.8107 | kWh/m2/yr
U values
(used in Building Part L)
| Walls | 0.18
| Windows | 1.4
| Floors | 0.15
| Roofs | 0.15
| Doors | 1.6
Room | Wall |  | Window |  | Floor |  | Ceiling |  | Door |  | Wall |  | Window |  | Floor |  | Ceiling |  | Doors |  | sum | Infiltration | Tai | Tao | Tai-Tao | Sum(UA)+nV/3 | Heat Loss | Heat Loss Rate(%) | Heat Loss | Heat loss
| Length | Height | Length | Height | Length | Width | Length | Width | Length | Width | U value | UA | U value | UA | U value | UA | U value | UA | U value | UA | UA | nV/3 | [6 empty] | per unit Area | x factor
| (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) | (Wm-2K-1) | (WK-1) |  | (WK-1) | (oC) | (oC) | (oC) | (WK-1) | (W) |  | (W/m2) | (W)
Classroom (70 seats)_ | 11 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 1.8 | 2 | 0.18 | 5.94 | 1.4 | 0 | 0.15 | 11.25 | 0.15 | 11.25 | 1.6 | 5.76 | 34.2 | 11.25 | 20 | -3 | 23 | 45.45 | 1045.35 | 3.8515 | 13.938 | 1254.42 | 3.8515
Classroom (70 seats)_ | 6 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 1.8 | 2 | 0.18 | 3.24 | 1.4 | 0 | 0.15 | 11.25 | 0.15 | 11.25 | 1.6 | 5.76 | 31.5 | 11.25 | 20 | -3 | 23 | 42.75 | 983.25 | 3.6227 | 13.11 | 1179.9 | 3.6227
Classroom (70 seats)_ | 6 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 1.8 | 2 | 0.18 | 3.24 | 1.4 | 0 | 0.15 | 11.25 | 0.15 | 11.25 | 1.6 | 5.76 | 31.5 | 11.25 | 20 | -3 | 23 | 42.75 | 983.25 | 3.6227 | 13.11 | 1179.9 | 3.6227
PC Lab (20 pcs) | 6 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 0.9 | 2 | 0.18 | 3.24 | 1.4 | 0 | 0.15 | 11.25 | 0.15 | 11.25 | 1.6 | 2.88 | 28.62 | 11.25 | 20 | -3 | 23 | 39.87 | 917.01 | 3.3787 | 12.2268 | 1100.412 | 3.3787
PC Lab (20 pcs) | 11 | 3 | 0 | 0 | 12.5 | 6 | 12.5 | 6 | 0.9 | 2 | 0.18 | 5.94 | 1.4 | 0 | 0.15 | 11.25 | 0.15 | 11.25 | 1.6 | 2.88 | 31.32 | 11.25 | 20 | -3 | 23 | 42.57 | 979.11 | 3.6075 | 13.0548 | 1174.932 | 3.6075
Stair 1 | 10 | 3 | 10 | 2.5 | 13 | 2.5 | 9 | 2.5 | 1.8 | 2 | 0.18 | 0.9 | 1.4 | 35 | 0.15 | 2.4375 | 0.15 | 1.6875 | 1.6 | 5.76 | 45.785 | 4.875 | 20 | -3 | 23 | 50.66 | 1165.18 | 4.293 | 35.8517 | 1398.216 | 4.293
Stair 2 | 10.5 | 3 | 0 | 0 | 3 | 7.5 | 3 | 7.5 | 0.9 | 2 | 0.18 | 5.67 | 1.4 | 0 | 0.15 | 2.4375 | 0.15 | 3.375 | 1.6 | 2.88 | 14.3625 | 2.4375 | 20 | -3 | 23 | 16.8 | 386.4 | 1.4237 | 17.1733 | 463.68 | 1.4237
Threater (150 seats) | 0 | 3 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.5 | 3.6 | 2 | 0.18 | 0 | 1.4 | 0 | 0.15 | 21.4708 | 0.15 | 21.4708 | 1.6 | 11.52 | 54.4616 | 21.4708 | 20 | -3 | 23 | 75.9325 | 1746.4467 | 6.4346 | 9.5827 | 2095.7361 | 6.4346
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.18 | 0.73772 | 1.4 | 24.5 | 0.15 | 9.5033 | 0.15 | 9.5033 | 1.6 | 5.76 | 50.0044 | 9.5033 | 20 | -3 | 23 | 59.5077 | 1368.6765 | 5.0428 | 11.3114 | 1642.4118 | 5.0428
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.18 | 0.73772 | 1.4 | 24.5 | 0.15 | 9.5033 | 0.15 | 9.5033 | 1.6 | 5.76 | 50.0044 | 9.5033 | 20 | -3 | 23 | 59.5077 | 1368.6765 | 5.0428 | 11.3114 | 1642.4118 | 5.0428
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.18 | 0.73772 | 1.4 | 24.5 | 0.15 | 9.5033 | 0.15 | 9.5033 | 1.6 | 5.76 | 50.0044 | 9.5033 | 20 | -3 | 23 | 59.5077 | 1368.6765 | 5.0428 | 11.3114 | 1642.4118 | 5.0428
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.18 | 0.73772 | 1.4 | 24.5 | 0.15 | 9.5033 | 0.15 | 9.5033 | 1.6 | 5.76 | 50.0044 | 9.5033 | 20 | -3 | 23 | 59.5077 | 1368.6765 | 5.0428 | 11.3114 | 1642.4118 | 5.0428
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.18 | 0.73772 | 1.4 | 24.5 | 0.15 | 9.5033 | 0.15 | 9.5033 | 1.6 | 5.76 | 50.0044 | 9.5033 | 20 | -3 | 23 | 59.5077 | 1368.6765 | 5.0428 | 11.3114 | 1642.4118 | 5.0428
Tutorial Classroom (62 seats) | 7.1995 | 3 | 7 | 2.5 | 11 | 11 | 11 | 11 | 1.8 | 2 | 0.18 | 0.73772 | 1.4 | 24.5 | 0.15 | 9.5033 | 0.15 | 9.5033 | 1.6 | 5.76 | 50.0044 | 9.5033 | 20 | -3 | 23 | 59.5077 | 1368.6765 | 5.0428 | 11.3114 | 1642.4118 | 5.0428
Café (24 seats) | 42.7 | 3 | 29 | 2.5 | 22.5 | 29.5 | 22.5 | 29.5 | 10.5 | 2 | 0.18 | 10.008 | 1.4 | 101.5 | 0.15 | 49.7812 | 0.15 | 49.7812 | 1.6 | 33.6 | 244.6705 | 49.7812 | 20 | -3 | 23 | 294.4518 | 6772.3903 | 24.9524 | 10.2032 | 8126.8683 | 24.9524
Toilet | 9 | 3 | 9 | 2.5 | 16 | 8.5 | 16 | 8.5 | 2.7 | 2 | 0.18 | 0.81 | 1.4 | 31.5 | 0.15 | 10.2 | 0.15 | 10.2 | 1.6 | 8.64 | 61.35 | 10.2 | 20 | -3 | 23 | 71.55 | 1645.65 | 6.0633 | 12.1004 | 1974.78 | 6.0633
Corridor1 | 6 | 3 | 0 | 0 | 25 | 3 | 25 | 3 | 3.6 | 2 | 0.18 | 3.24 | 1.4 | 0 | 0.15 | 11.25 | 0.15 | 11.25 | 1.6 | 11.52 | 37.26 | 11.25 | 20 | -3 | 23 | 48.51 | 1115.73 | 4.1108 | 14.8764 | 1338.876 | 4.1108
Corridor2 | 0 | 0 | 0 | 0 | 27.5 | 3 | 27.5 | 3 | 1.8 | 2 | 0.18 | 0 | 1.4 | 0 | 0.15 | 12.375 | 0.15 | 12.375 | 1.6 | 5.76 | 30.51 | 0 | 20 | -3 | 23 | 30.51 | 701.73 | 2.5855 | 8.5058 | 842.076 | 2.5855
Corridor3 | 0 | 0 | 0 | 0 | 27.5 | 3 | 27.5 | 3 | 0 | 0 | 0.18 | 0 | 1.4 | 0 | 0.15 | 10.6029 | 0.15 | 10.6029 | 1.6 | 0 | 21.2058 | 0 | 20 | -3 | 23 | 21.2058 | 487.7323 | 1.797 | 5.9119 | 585.2787 | 1.797
[26 empty] | Total Heat Loss | 27141.2883 |  | 17.3418 | 32569.546
|  | Floor |  |  | Floor Area (m2)
|  | stair 1 |  |  | 16.25
|  | Threater |  |  | 143.1388
|  | Tutorial Classroom |  |  | 63.3555
|  | café |  |  | 331.875
|  | Toilet |  |  | 68
|  | Corridor3 |  |  | 70.6858
|  | PC |  |  | 75
|  | Corridor2 |  |  | 82.5
|  | Corridor1 |  |  | 75

## Htg_hot_water
Hot water load |  | Floor area | 1565.0824 | m2 |  | (assuming central hot water storage tank)
(fed from boiler)
No occup | 461 |  | Days/yr | 200 |  | (days/year building is occupied)
Usage/occ | 7 | litres | HW eff | 0.75 |  | (thermal efficiency of hot water system)
cpwater | 4187 | W/J/kg |  | 75 | %
DT | 50 | deg C | =(60 -10)
Pre-heat time (h) | 2 | h
Hot water load | 125106.0093 | W
| 125.106 | kW
Hot water energy | 900763266.6667 | J/day
(per day) | 250.212 | kWh/day
Hot water energy | 50042.4037 | kWh/year
(annual)
| 31.9743 | kWh/m2/yr
Classroom (70 seats)_ | 40
Classroom (70 seats)_ | 40
Classroom (70 seats)_ | 40
PC Lab (20 pcs) | 15
PC Lab (20 pcs) | 15
Stair 1 | 0
Stair 2 | 0
Threater (150 seats) | 100
Tutorial Classroom (62 seats) | 30
Tutorial Classroom (62 seats) | 30
Tutorial Classroom (62 seats) | 30
Tutorial Classroom (62 seats) | 30
Tutorial Classroom (62 seats) | 30
Tutorial Classroom (62 seats) | 30
Café (24 seats) | 20
Toilet | 2
Corridor1 | 3
Corridor2 | 3
Corridor3 | 3
461

## Th_energy1
Energy use (house)
Thermal energy
| Heating | Q= | Heat loss | 82377.0535 | W | Ti | 20 |  | NDD | 2360
| (Perimeter) |  |  |  |  | To | -3
[6 empty] | DT | 23
|  |  | Q/DT | 3581.611 | W/oC
Afloor | 1565.0824 | m2
|  | Ehtg | [Sum UA + nV/3]*24*NDD/1000 |  |  |  | E/Afloor | (kWh/m2/year)
|  | Ehtg | 202862.4483 | kWh/year |  |  | 129.6177
| Hot water | Ehw | 50042.4037 | kWh/year |  |  | 31.9743
|  | E_solar | 26931.15 | kWh/year
|  | Etotal | 225973.702 | kWh/year |  |  | 144.3845
| Fuel: | Kersone | 44000000 | J/kg
|  |  | 12.2222 | kWh/kg
| Fuel consumption |  | 18488.7574 | kg/year
| Density | 800 | kg/m3 | (Kerosene) |  |  | 0.8kg/l
| Fuel consumption |  | 23110.9468 | litres | /year
| Cost/l |  | 1.4
| Cost | € | 32355.3255 |  | /year | € | 20.6732 | /m2/year

## Th_energy2
Energy use (house)
Thermal energy (Improved)
| Heating | Q= | Heat loss | 27141.2883 | W | Ti | 20 |  | NDD | 2360
| (Perimeter) |  |  |  |  | To | -3
[6 empty] | DT | 23
|  |  | Q/DT | 1180.056 | W/oC
Afloor | 1565.0824 | m2
|  | Ehtg | [Sum UA + nV/3]*24*NDD/1000 |  |  |  | E/Afloor | (kWh/m2/year)
|  | Ehtg | 66838.3726 | kWh/year |  |  | 42.706
| Hot water | Ehw | 50042.4037 | kWh/year |  |  | 31.9743
|  | E_solar | 77003.1 | kWh/year
|  | Etotal | 39877.6763 | kWh/year |  |  | 25.4796
| Fuel: | Kersone | 44000000 | J/kg
|  |  | 12.2222 | kWh/kg
| Fuel consumption |  | 3262.719 | kg/year
| Density | 800 | kg/m3 | (Kerosene) |  |  | 0.8kg/l
| Fuel consumption |  | 4078.3987 | litres | /year
| Cost/l |  | 1.4
| Cost | € | 5709.7582 |  | /year | € | 3.6482 | /m2/year

## Electricity Load1
Electrical loads
Load |  | P/A | Area (fl)/Quan. | Op time | Diversity | Pt | Total
|  | (W/m2) | (m2)/(pc) | 0 | 0.7 | (Wh) | (kWh)
Classroom | Lights | 10 | 75 | 5 | 0.7 | 2625 | 2.625
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Router, Switch ports | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Controls | 1 | 75 | 5 | 0.7 | 262.5 | 0.2625
Classroom | Lights | 10 | 75 | 5 | 0.7 | 2625 | 2.625
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Router, Switch ports | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Controls | 1 | 75 | 5 | 0.7 | 262.5 | 0.2625
Classroom | Lights | 10 | 75 | 5 | 0.7 | 2625 | 2.625
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Router, Switch ports | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Controls | 1 | 75 | 5 | 0.7 | 262.5 | 0.2625
PC Lab | Lights | 10 | 75 | 5 | 0.7 | 2625 | 2.625
| PC | 100 | 20 | 5 | 0.7 | 7000 | 7
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Network Switches | 5 | 75 | 5 | 0.7 | 1312.5 | 1.3125
| Controls | 1 | 75 | 5 | 0.7 | 262.5 | 0.2625
PC Lab | Lights | 10 | 75 | 5 | 0.7 | 2625 | 2.625
| PC | 100 | 20 | 5 | 0.7 | 7000 | 7
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 75 | 5 | 0.7 | 525 | 0.525
| Network Switches | 5 | 75 | 5 | 0.7 | 1312.5 | 1.3125
| Controls | 1 | 75 | 5 | 0.7 | 262.5 | 0.2625
Theater | Lights | 10 | 143.1388 | 3 | 0.7 | 3005.9151 | 3.0059
| Projector，Amplifiers | 200 | 1 | 3 | 0.7 | 420 | 0.42
| Audio system, spotlighting | 1000 | 1 | 3 | 0.7 | 2100 | 2.1
| Pumps | 2 | 143.1388 | 3 | 0.7 | 601.183 | 0.60118
| Media equipment | 5 | 143.1388 | 3 | 0.7 | 1502.9576 | 1.503
| Controls | 1 | 143.1388 | 3 | 0.7 | 300.5915 | 0.30059
Tutorial Classroom | Lights | 10 | 63.3555 | 5 | 0.7 | 2217.4408 | 2.2174
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Router, Switch ports | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Controls | 1 | 63.3555 | 5 | 0.7 | 221.7441 | 0.22174
Tutorial Classroom | Lights | 10 | 63.3555 | 5 | 0.7 | 2217.4408 | 2.2174
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 63.36 | 5 | 0.7 | 443.52 | 0.44352
| Router, Switch ports | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Controls | 1 | 63.3555 | 5 | 0.7 | 221.7441 | 0.22174
Tutorial Classroom | Lights | 10 | 63.3555 | 5 | 0.7 | 2217.4408 | 2.2174
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 63.36 | 5 | 0.7 | 443.52 | 0.44352
| Router, Switch ports | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Controls | 1 | 63.3555 | 5 | 0.7 | 221.7441 | 0.22174
Tutorial Classroom | Lights | 10 | 63.3555 | 5 | 0.7 | 2217.4408 | 2.2174
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 63.36 | 5 | 0.7 | 443.52 | 0.44352
| Router, Switch ports | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Controls | 1 | 63.3555 | 5 | 0.7 | 221.7441 | 0.22174
Tutorial Classroom | Lights | 10 | 63.3555 | 5 | 0.7 | 2217.4408 | 2.2174
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 63.36 | 5 | 0.7 | 443.52 | 0.44352
| Router, Switch ports | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Controls | 1 | 63.3555 | 5 | 0.7 | 221.7441 | 0.22174
Tutorial Classroom | Lights | 10 | 63.3555 | 5 | 0.7 | 2217.4408 | 2.2174
| PC | 100 | 1 | 5 | 0.7 | 350 | 0.35
| Projector | 200 | 1 | 5 | 0.7 | 700 | 0.7
| Pumps | 2 | 63.36 | 5 | 0.7 | 443.52 | 0.44352
| Router, Switch ports | 2 | 63.3555 | 5 | 0.7 | 443.4882 | 0.44349
| Controls | 1 | 63.3555 | 5 | 0.7 | 221.7441 | 0.22174
Toilet | Lights | 10 | 68 | 2 | 0.7 | 952 | 0.952
| Hand dryer | 1200 | 1 | 2 | 0.7 | 1680 | 1.68
| Pumps | 2 | 68 | 2 | 0.7 | 190.4 | 0.1904
Café | Lights | 10 | 331.875 | 3 | 0.7 | 6969.375 | 6.9694
| Coffee machine | 1500 | 1 | 3 | 0.7 | 3150 | 3.15
| Refrigerator | 300 | 1 | 3 | 0.7 | 630 | 0.63
| Microwave | 1000 | 1 | 3 | 0.7 | 2100 | 2.1
| Kettle | 1500 | 1 | 3 | 0.7 | 3150 | 3.15
| Pumps | 2 | 331.875 | 3 | 0.7 | 1393.875 | 1.3939
| Router, POS | 100 | 1 | 3 | 0.7 | 210 | 0.21
| Plug loads | 5 | 1 | 3 | 0.7 | 10.5 | 0.0105
Corridor | Lights | 10 | 228.1858 | 8 | 0.7 | 12778.4067 | 12.7784
| Fire Alarm | 100 | 1 | 24 | 0.7 | 1680 | 1.68
Totals | [5 empty] | 108894.8305 | 108.8948 | kWh
|  | Days/year | 200 | Annual electrical energy |  |  | 21778.9661 | kWh/year

## Electricity Load2
Electrical loads
Load |  | P/A | Area (fl)/Quan. | Op time | Diversity | Pt | Total
|  | (W/m2) | (m2)/(pc) | 0 |  | (Wh) | (kWh)
Classroom | LED Lights | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Router, Switch ports | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Controls | 1 | 75 | 5 | 0.5 | 187.5 | 0.1875
Classroom | LED Lights | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Router, Switch ports | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Controls | 1 | 75 | 5 | 0.5 | 187.5 | 0.1875
Classroom | LED Lights | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Router, Switch ports | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Controls | 1 | 75 | 5 | 0.5 | 187.5 | 0.1875
PC Lab | LED Lights | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| PC(enable sleep mode) | 60 | 20 | 5 | 0.5 | 3000 | 3
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Network Switches | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| Controls | 1 | 75 | 5 | 0.5 | 187.5 | 0.1875
PC Lab | LED Lights | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| PC(enable sleep mode) | 60 | 20 | 5 | 0.5 | 3000 | 3
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 75 | 5 | 0.5 | 375 | 0.375
| Network Switches | 5 | 75 | 5 | 0.5 | 937.5 | 0.9375
| Controls | 1 | 75 | 5 | 0.5 | 187.5 | 0.1875
Theater | LED Lights | 5 | 143.1388 | 3 | 0.5 | 1073.5411 | 1.0735
| LED Projector，Amplifiers | 150 | 1 | 3 | 0.5 | 225 | 0.225
| Audio system, spotlighting | 1000 | 1 | 3 | 0.5 | 1500 | 1.5
| Pumps | 2 | 143.1388 | 3 | 0.5 | 429.4164 | 0.42942
| Media equipment | 5 | 143.1388 | 3 | 0.5 | 1073.5411 | 1.0735
| Controls | 1 | 143.1388 | 3 | 0.5 | 214.7082 | 0.21471
Tutorial Classroom | LED Lights | 5 | 63.3555 | 5 | 0.5 | 791.9431 | 0.79194
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Router, Switch ports | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Controls | 1 | 63.3555 | 5 | 0.5 | 158.3886 | 0.15839
Tutorial Classroom | LED Lights | 5 | 63.3555 | 5 | 0.5 | 791.9431 | 0.79194
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 63.36 | 5 | 0.5 | 316.8 | 0.3168
| Router, Switch ports | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Controls | 1 | 63.3555 | 5 | 0.5 | 158.3886 | 0.15839
Tutorial Classroom | LED Lights | 5 | 63.3555 | 5 | 0.5 | 791.9431 | 0.79194
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 63.36 | 5 | 0.5 | 316.8 | 0.3168
| Router, Switch ports | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Controls | 1 | 63.3555 | 5 | 0.5 | 158.3886 | 0.15839
Tutorial Classroom | LED Lights | 5 | 63.3555 | 5 | 0.5 | 791.9431 | 0.79194
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 63.36 | 5 | 0.5 | 316.8 | 0.3168
| Router, Switch ports | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Controls | 1 | 63.3555 | 5 | 0.5 | 158.3886 | 0.15839
Tutorial Classroom | LED Lights | 5 | 63.3555 | 5 | 0.5 | 791.9431 | 0.79194
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 63.36 | 5 | 0.5 | 316.8 | 0.3168
| Router, Switch ports | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Controls | 1 | 63.3555 | 5 | 0.5 | 158.3886 | 0.15839
Tutorial Classroom | LED Lights | 5 | 63.3555 | 5 | 0.5 | 791.9431 | 0.79194
| PC(enable sleep mode) | 60 | 1 | 5 | 0.5 | 150 | 0.15
| LED Projector | 150 | 1 | 5 | 0.5 | 375 | 0.375
| Pumps | 2 | 63.36 | 5 | 0.5 | 316.8 | 0.3168
| Router, Switch ports | 2 | 63.3555 | 5 | 0.5 | 316.7773 | 0.31678
| Controls | 1 | 63.3555 | 5 | 0.5 | 158.3886 | 0.15839
Toilet | LED Lights | 5 | 68 | 2 | 0.5 | 340 | 0.34
| Hand dryer | 1200 | 1 | 2 | 0.5 | 1200 | 1.2
| Pumps | 2 | 68 | 2 | 0.5 | 136 | 0.136
Café | LED Lights | 5 | 331.875 | 3 | 0.5 | 2489.0625 | 2.4891
| Coffee machine | 1500 | 1 | 3 | 0.5 | 2250 | 2.25
| Refrigerator | 300 | 1 | 3 | 0.5 | 450 | 0.45
| Microwave | 1000 | 1 | 3 | 0.5 | 1500 | 1.5
| Kettle | 1500 | 1 | 3 | 0.5 | 2250 | 2.25
| Pumps | 2 | 331.875 | 3 | 0.5 | 995.625 | 0.99562
| Router, POS | 100 | 1 | 3 | 0.5 | 150 | 0.15
| Plug loads | 5 | 1 | 3 | 0.5 | 7.5 | 0.0075
Corridor | LED Lights | 5 | 228.1858 | 8 | 0.5 | 4563.7167 | 4.5637
| Fire Alarm | 100 | 1 | 24 | 0.5 | 1200 | 1.2
Totals | [5 empty] | 53526.5426 | 53.5265 | kWh
|  | Days/year | 200 | Annual electrical energy |  |  | 10705.3085 | kWh/year

## Primary_Energy1
Primary energy use |  |  | Area | 1565.0824
Primary energy factors
| PEF (thermal) | 1.1
2
| Demand thermal energy |  | 144.3845 | kWh/m2/year
| Demand electrical energy |  | 13.9155 | kWh/m2/year
| Primary energy (thermal) |  | 158.823
| Primary energy (elect) |  | 27.8311
| Total primary energy |  | 186.6541 | kWh/m2/year

## Primary_Energy2
Primary energy use |  |  | Area | 1565.0824
Primary energy factors
| PEF (thermal) | 1.1
2
| Demand thermal energy |  | 25.4796 | kWh/m2/year
| Demand electrical energy |  | 6.8401 | kWh/m2/year
| Primary energy (thermal) |  | 28.0276
| Primary energy (elect) |  | 13.6802
| Total primary energy |  | 41.7077 | kWh/m2/year

## Tmax_final2
EM & HT | Improved
HVAC
|  | T (oC) | Fan effi | 0.7 |  | Pressure | 500 | pa | T1 | 0 | oC
| Supply | 15 | ρ | 1.2 | kg/m³ | g | 0.3 |  | T2 | 10 | oC
| Room | 22 | To | 18 | oC | Cp air | 1020 | J /(kg K) | T3 | 30 | oC
| Room | Heat gains | Load (s) | Area | Qs | Quan. | Ql |  | Daily Solar Irradiation estimate (June) |  |  |  | Q_totalheat gain | Vol flow | Mass flow | airflow | Pfan | Q_preheat | Q_coil
|  |  | (W/m2) | (m2) | (W) | Pcs | (W) |  | Time(h) | Irradiation (w/m2) |  |  | W | m3/s | kg/s | a/c/h | W | W | W
| Classroom | Lights | 10 | 75 | 750 |  |  |  | 0 | 0 |  | Classroom | 6650 | 0.77614 | 0.93137 | 12.4183 | 554.3884 | 9500 | 253333.3333
|  | Occupants | 140 |  |  | 40 | 5600 |  | 1 | 0 |  | Classroom | 6650 | 0.77614 | 0.93137 | 12.4183 | 554.3884 | 9500 | 253333.3333
|  | Projector | 200 |  |  |  | 200 |  | 2 | 0 |  | Classroom | 6650 | 0.77614 | 0.93137 | 12.4183 | 554.3884 | 9500 | 253333.3333
|  | PC | 100 |  |  | 1 | 100 |  | 3 | 0 |  | PC Lab | 5050 | 0.5894 | 0.70728 | 9.4304 | 421.0017 | 7214.2857 | 192380.9524
| Classroom | Lights | 10 | 75 | 750 |  |  |  | 4 | 0 |  | PC Lab | 5050 | 0.5894 | 0.70728 | 9.4304 | 421.0017 | 7214.2857 | 192380.9524
|  | Occupants | 140 |  |  | 40 | 5600 |  | 5 | 142.45 |  | Threater | 15731.3882 | 1.8361 | 2.2033 | 15.3926 | 1311.4736 | 22473.4116 | 314008.6301
|  | Projector | 200 |  |  |  | 200 |  | 6 | 253.46 |  | Tutorial Classroom | 5148.6759 | 0.60092 | 0.7211 | 5.0378 | 429.228 | 7355.2513 | 102770.8836
|  | PC | 100 |  |  | 1 | 100 |  | 7 | 340.45 |  | Tutorial Classroom | 5148.6759 | 0.60092 | 0.7211 | 11.3819 | 429.228 | 7355.2513 | 232190.0025
| Classroom | Lights | 10 | 75 | 750 |  |  |  | 8 | 376.93 |  | Tutorial Classroom | 5148.6759 | 0.60092 | 0.7211 | 11.3819 | 429.228 | 7355.2513 | 232190.0025
|  | Occupants | 140 |  |  | 40 | 5600 |  | 9 | 362.07 |  | Tutorial Classroom | 5148.6759 | 0.60092 | 0.7211 | 11.3819 | 429.228 | 7355.2513 | 232190.0025
|  | Projector | 200 |  |  |  | 200 |  | 10 | 317.13 |  | Tutorial Classroom | 5148.6759 | 0.60092 | 0.7211 | 11.3819 | 429.228 | 7355.2513 | 232190.0025
|  | PC | 100 |  |  |  | 100 |  | 11 | 268.84 |  | Tutorial Classroom | 5148.6759 | 0.60092 | 0.7211 | 11.3819 | 429.228 | 7355.2513 | 232190.0025
| PC Lab | Lights | 10 | 75 | 750 |  |  |  | 12 | 205.96 |  | Café | 6181.3957 | 0.72145 | 0.86574 | 13.6648 | 515.3224 | 8830.5652 | 278762.5994
|  | Occupants | 140 |  |  | 15 | 2100 |  | 13 | 130.23 |  | Toilet | 979.4418 | 0.11431 | 0.13718 | 0.41334 | 81.6528 | 1399.2025 | 8432.1055 | Efan | 1456.8517 |  | kWh/yr
|  | Projector | 200 |  |  | 1 | 200 |  | 14 | 122.55 |  | Corridor | 3541.8583 | 0.41338 | 0.49606 | 2.1739 | 295.273 | 5059.7976 | 44348.0433 | Epreheat+Ecoil |  | 1412.8254 | kWh/yr
|  | PC | 100 |  |  | 20 | 2000 |  | 15 | 112.18 | [5 empty] | Annual | 7284.2586 | 3178857.2352 | kWh/yr
|  | Lights | 10 | 75 | 750 |  |  |  | 16 | 95.6
| PC Lab | Occupants | 140 |  |  | 15 | 2100 |  | 17 | 72.54 |  |  | Q_totalheat gain | Vol flow | Mass flow | airflow | sumUA+nV/3 | Ti -To | Ti max | Pfan | Q_preheat | Q_coil
|  | Projector | 200 |  |  |  | 200 |  | 18 | 48.66 |  |  | W | m3/s | kg/s | a/c/h |  | oC | oC | W | W | W
|  | PC | 100 |  |  | 20 | 2000 |  | 19 | 24.66 |  | PC Lab | 5050 | 0.3125 | 0.375 | 5 | 39.87 | 11.9563 | 29.9563 | 223.2143 | 3825 | 7650
|  | Lights | 10 | 143.1388 | 1431.3882 |  |  |  | 20 | 6.55 |  | PC Lab | 5050 | 0.3125 | 0.375 | 5 | 42.57 | 11.8804 | 29.8804 | 223.2143 | 3825 | 7650
| Threater | Occupants | 140 |  |  | 100 | 14000 |  | 21 | 0 |  | Threater | 15731.3882 | 0.95426 | 1.1451 | 8 | 75.9325 | 12.6464 | 30.6464 | 681.6134 | 11680.1273 | 23360.2547
|  | Projector | 200 |  |  |  | 200 |  | 22 | 0 |  | Tutorial Classroom | 5148.6759 | 0.36957 | 0.44349 | 7 | 59.5077 | 10.0586 | 28.0586 | 263.981 | 4523.5793 | 9047.1585
|  | PC | 100 |  |  |  | 100 |  | 23 | 0 | source | Tutorial Classroom | 5148.6759 | 0.36957 | 0.44349 | 7 | 59.5077 | 10.0586 | 28.0586 | 263.981 | 4523.5793 | 9047.1585
|  | Lights | 10 | 63.3555 | 633.5545 |  |  |  | Total | 2.8803 | Met.ie | Tutorial Classroom | 5148.6759 | 0.31678 | 0.38013 | 6 | 59.5077 | 11.512 | 29.512 | 226.2695 | 3877.3537 | 7754.7073
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200 |  |  |  |  | Tutorial Classroom | 5148.6759 | 0.31678 | 0.38013 | 6 | 59.5077 | 11.512 | 29.512 | 226.2695 | 3877.3537 | 7754.7073
|  | Projector | 200 |  |  |  | 200 |  |  |  |  | Tutorial Classroom | 5148.6759 | 0.31678 | 0.38013 | 6 | 59.5077 | 11.512 | 29.512 | 226.2695 | 3877.3537 | 7754.7073
|  | PC | 100 |  |  |  | 100 |  |  |  |  | Tutorial Classroom | 5148.6759 | 0.31678 | 0.38013 | 6 | 59.5077 | 11.512 | 29.512 | 226.2695 | 3877.3537 | 7754.7073
|  | solar | 0.86408 | 17.5 | 15.1214 | [6 empty] | Café | 6181.3957 | 0.27656 | 0.33187 | 1 | 294.4518 | 9.7658 | 27.7658 | 197.5446 | 3385.125 | 6770.25
|  | Lights | 10 | 63.3555 | 633.5545 | [6 empty] | Classroom | 6650 | 0.4375 | 0.525 | 7 | 45.45 | 11.4468 | 29.4468 | 312.5 | 5355 | 10710
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200 |  |  |  |  | Classroom | 6650 | 0.4375 | 0.525 | 7 | 42.75 | 11.5002 | 29.5002 | 312.5 | 5355 | 10710
|  | Projector | 200 |  |  |  | 200 |  |  |  |  | Classroom | 6650 | 0.375 | 0.45 | 6 | 42.75 | 13.2536 | 31.2536 | 267.8571 | 4590 | 9180
|  | PC | 100 |  |  |  | 100 |  |  |  |  | Toilet | 979.4418 | 0.056667 | 0.068 | 1 | 71.55 | 6.9508 | 24.9508 | 40.4762 | 693.6 | 1387.2
|  | solar | 0.86408 | 17.5 | 15.1214 | [6 empty] | Corridor | 3541.8583 | 0.19015 | 0.22819 | 1 | 100.2258 | 10.637 | 28.637 | 135.8249 | 2327.4955 | 4654.991
|  | Lights | 10 | 63.3555 | 633.5545 | [13 empty] | Annual | 3827.7848 | 196778.7629 | kWh/yr
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200 | [11 empty] | Efan | 765.557 |  | kWh/yr
|  | Projector | 200 |  |  |  | 200 | [11 empty] | Epreheat+Ecoil |  | 87.4572 | kWh/yr
|  | PC | 100 |  |  |  | 100
|  | solar | 0.86408 | 17.5 | 15.1214
|  | Lights | 10 | 63.3555 | 633.5545
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200
|  | Projector | 200 |  |  |  | 200
|  | PC | 100 |  |  |  | 100
|  | solar | 0.86408 | 17.5 | 15.1214
|  | Lights | 10 | 63.3555 | 633.5545
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200
|  | Projector | 200 |  |  |  | 200
|  | PC | 100 |  |  |  | 100
|  | solar | 0.86408 | 17.5 | 15.1214
|  | Lights | 10 | 63.3555 | 633.5545
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200
|  | Projector | 200 |  |  |  | 200
|  | PC | 150 |  |  |  | 150
|  | solar | 0.86408 | 17.5 | 15.1214
|  | Lights | 10 | 331.875 | 3318.75
| Café | Occupants | 140 |  |  | 20 | 2800
|  | solar | 0.86408 | 72.5 | 62.6457
| Toilet | solar | 0.86408 | 22.5 | 19.4418
|  | Lights | 10 | 68 | 680
|  | Occupants | 140 |  |  | 2 | 280
| Corridor | Lights | 10 | 228.1858 | 2281.8583
|  | Occupants | 140 |  |  | 9 | 1260
|  |  |  | Sum | 15436.1392 | W | 71990
https://re.jrc.ec.europa.eu/pvg_tools/en/
|  |  |  | Qtotal | 87426.1392

## Tmax_final1
EM & HT | Original
HVAC
|  | T (oC) | Fan effi | 0.7 |  | Pressure | 500 | pa | T1 | 0 | oC
| Supply | 15 | ρ | 1.2 | kg/m³ | g | 0.6 |  | T2 | 10 | oC
| Room | 22 | To | 20 | oC | Cp air | 1020 | J /(kg K) | T3 | 30 | oC
| Room | Heat gains | Load (s) | Area | Qs | Quan. | Ql |  | Daily Solar Irradiation estimate (June) |  |  |  | Q_totalheat gain | Vol flow | Mass flow | airflow | Pfan | Q_preheat | Q_coil
|  |  | (W/m2) | (m2) | (W) | Pcs | (W) |  | Time(h) | Irradiation (w/m2) |  |  | W | m3/s | kg/s | a/c/h | W | W | W
|  | Lights | 10 | 75 | 750 |  |  |  | 0 | 0 |  | Classroom | 6650 | 0.77614 | 0.93137 | 12.4183 | 554.3884 | 9500 | 253333.3333
|  | Occupants | 140 |  |  | 40 | 5600 |  | 1 | 0 |  | Classroom | 6650 | 0.77614 | 0.93137 | 12.4183 | 554.3884 | 9500 | 253333.3333
| Classroom | Projector | 200 |  |  |  | 200 |  | 2 | 0 |  | Classroom | 6650 | 0.77614 | 0.93137 | 12.4183 | 554.3884 | 9500 | 253333.3333
|  | PC | 100 |  |  | 1 | 100 |  | 3 | 0 |  | PC Lab | 5050 | 0.5894 | 0.70728 | 9.4304 | 421.0017 | 7214.2857 | 192380.9524
|  | Lights | 10 | 75 | 750 |  |  |  | 4 | 0 |  | PC Lab | 5050 | 0.5894 | 0.70728 | 9.4304 | 421.0017 | 7214.2857 | 192380.9524
|  | Occupants | 140 |  |  | 40 | 5600 |  | 5 | 142.45 |  | Threater | 15731.3882 | 1.8361 | 2.2033 | 15.3926 | 1311.4736 | 22473.4116 | 314008.6301
| Classroom | Projector | 200 |  |  |  | 200 |  | 6 | 253.46 |  | Tutorial Classroom | 5163.7972 | 0.60268 | 0.72322 | 11.4153 | 430.4886 | 7376.8532 | 232871.9312
|  | PC | 100 |  |  | 1 | 100 |  | 7 | 340.45 |  | Tutorial Classroom | 5163.7972 | 0.60268 | 0.72322 | 11.4153 | 430.4886 | 7376.8532 | 232871.9312
|  | Lights | 10 | 75 | 750 |  |  |  | 8 | 376.93 |  | Tutorial Classroom | 5163.7972 | 0.60268 | 0.72322 | 11.4153 | 430.4886 | 7376.8532 | 232871.9312
|  | Occupants | 140 |  |  | 40 | 5600 |  | 9 | 362.07 |  | Tutorial Classroom | 5163.7972 | 0.60268 | 0.72322 | 11.4153 | 430.4886 | 7376.8532 | 232871.9312
| Classroom | Projector | 200 |  |  |  | 200 |  | 10 | 317.13 |  | Tutorial Classroom | 5163.7972 | 0.60268 | 0.72322 | 11.4153 | 430.4886 | 7376.8532 | 232871.9312
|  | PC | 100 |  |  |  | 100 |  | 11 | 268.84 |  | Tutorial Classroom | 5163.7972 | 0.60268 | 0.72322 | 11.4153 | 430.4886 | 7376.8532 | 232871.9312
| PC Lab | Lights | 10 | 75 | 750 |  |  |  | 12 | 205.96 |  | Café | 6244.0413 | 0.72876 | 0.87452 | 2.6351 | 520.545 | 8920.059 | 53755.5345 | Efan | 1459.7331 |  | kWh/yr
|  | Occupants | 140 |  |  | 15 | 2100 |  | 13 | 130.23 |  | Toilet | 998.8835 | 0.11658 | 0.1399 | 2.0573 | 83.2736 | 1426.9764 | 41969.8954 | Epreheat+Ecoil |  | 1387.1758 | kWh/yr
|  | Projector | 200 |  |  |  | 200 |  | 14 | 122.55 |  | Corridor | 3541.8583 | 0.41338 | 0.49606 | 2.1739 | 295.273 | 5059.7976 | 44348.0433
|  | PC | 100 |  |  | 20 | 2000 |  | 15 | 112.18 |  |  | 87548.9548 |  |  | Annual | 7298.6657 | 3121145.5307 | W
|  | Lights | 10 | 75 | 750 |  |  |  | 16 | 95.6
| PC Lab | Occupants | 140 |  |  | 15 | 2100 |  | 17 | 72.54 |  |  | Q_totalheat gain | Vol flow | Mass flow | airflow | sumUA+nV/3 | Ti -To | Ti max | Pfan | Q_preheat | Q_coil
|  | Projector | 200 |  |  |  | 200 |  | 18 | 48.66 |  |  | W | m3/s | kg/s | a/c/h |  | oC | oC | W | W | W
|  | PC | 100 |  |  | 20 | 2000 |  | 19 | 24.66 |  | PC Lab | 5050 | 0.0625 | 0.075 | 1 | 151.4909 | 22.15 | 42.15 | 44.6429 | 765 | 1530
|  | Lights | 10 | 143.1388 | 1431.3882 |  | 0 |  | 20 | 6.55 |  | PC Lab | 5050 | 0.0625 | 0.075 | 1 | 155.6834 | 21.75 | 41.75 | 44.6429 | 765 | 1530
| Threater | Occupants | 140 |  |  | 100 | 14000 |  | 21 | 0 |  | Threater | 15731.3882 | 0.11928 | 0.14314 | 1 | 287.8037 | 36.2637 | 56.2637 | 85.2017 | 1460.0159 | 2920.0318
|  | Projector | 200 |  |  |  | 200 |  | 22 | 0 |  | Tutorial Classroom | 5163.7972 | 0.052796 | 0.063355 | 1 | 167.9409 | 22.2038 | 42.2038 | 37.7116 | 646.2256 | 1292.4512
|  | PC | 100 |  |  |  | 100 |  | 23 | 0 | source | Tutorial Classroom | 5163.7972 | 0.052796 | 0.063355 | 1 | 167.9409 | 22.2038 | 42.2038 | 37.7116 | 646.2256 | 1292.4512
|  | Lights | 10 | 63.3555 | 633.5545 |  |  |  | Total | 2.8803 | Met.ie | Tutorial Classroom | 5163.7972 | 0.052796 | 0.063355 | 1 | 167.9409 | 22.2038 | 42.2038 | 37.7116 | 646.2256 | 1292.4512
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200 |  |  |  |  | Tutorial Classroom | 5163.7972 | 0.052796 | 0.063355 | 1 | 167.9409 | 22.2038 | 42.2038 | 37.7116 | 646.2256 | 1292.4512
|  | Projector | 200 |  |  |  | 200 |  |  |  |  | Tutorial Classroom | 5163.7972 | 0.052796 | 0.063355 | 1 | 167.9409 | 22.2038 | 42.2038 | 37.7116 | 646.2256 | 1292.4512
|  | PC | 100 |  |  |  | 100 |  |  |  |  | Tutorial Classroom | 5163.7972 | 0.052796 | 0.063355 | 1 | 167.9409 | 22.2038 | 42.2038 | 37.7116 | 646.2256 | 1292.4512
|  | solar | 1.7282 | 17.5 | 30.2427 | [6 empty] | Café | 6244.0413 | 0.27656 | 0.33187 | 1 | 851.8025 | 5.2457 | 25.2457 | 197.5446 | 3385.125 | 6770.25
|  | Lights | 10 | 63.3555 | 633.5545 | [6 empty] | Classroom | 6650 | 0.0625 | 0.075 | 1 | 159.6434 | 28.1609 | 48.1609 | 44.6429 | 765 | 1530
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200 |  |  |  |  | Classroom | 6650 | 0.0625 | 0.075 | 1 | 155.4509 | 28.6699 | 48.6699 | 44.6429 | 765 | 1530
|  | Projector | 200 |  |  |  | 200 |  |  |  |  | Classroom | 6650 | 0.0625 | 0.075 | 1 | 155.4509 | 28.6699 | 48.6699 | 44.6429 | 765 | 1530
|  | PC | 100 |  |  |  | 100 |  |  |  |  | Toilet | 998.8835 | 0.056667 | 0.068 | 1 | 191.8377 | 3.8242 | 23.8242 | 40.4762 | 693.6 | 1387.2
|  | solar | 1.7282 | 17.5 | 30.2427 | [6 empty] | Corridor | 3541.8583 | 0.19015 | 0.22819 | 1 | 309.1582 | 6.5359 | 26.5359 | 135.8249 | 2327.4955 | 4654.991
|  | Lights | 10 | 63.3555 | 633.5545 | [7 empty] | 87548.9548 | [5 empty] | Total | 908.5312 | 46705.7702
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200 | [11 empty] | Efan | 181.7062 |  | kWh/yr
|  | Projector | 200 |  |  |  | 200 | [11 empty] | Epreheat+Ecoil |  | 20.7581 | kWh/yr
|  | PC | 100 |  |  |  | 100
|  | solar | 1.7282 | 17.5 | 30.2427
|  | Lights | 10 | 63.3555 | 633.5545
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200
|  | Projector | 200 |  |  |  | 200
|  | PC | 100 |  |  |  | 100
|  | solar | 1.7282 | 17.5 | 30.2427
|  | Lights | 10 | 63.3555 | 633.5545
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200
|  | Projector | 200 |  |  |  | 200
|  | PC | 100 |  |  |  | 100
|  | solar | 1.7282 | 17.5 | 30.2427
|  | Lights | 10 | 63.3555 | 633.5545
| Tutorial Classroom | Occupants | 140 |  |  | 30 | 4200
|  | Projector | 200 |  |  |  | 200
|  | PC | 150 |  |  |  | 150
|  | solar | 1.7282 | 17.5 | 30.2427
|  | Lights | 10 | 331.875 | 3318.75
| Café | Occupants | 140 |  |  | 20 | 2800
|  | solar | 1.7282 | 72.5 | 125.2913
|  | solar | 1.7282 | 22.5 | 38.8835
| Toilet | Lights | 10 | 68 | 680
|  | Occupants | 140 |  |  | 2 | 280
|  | Lights | 10 | 228.1858 | 2281.8583
| Corridor | Occupants | 140 |  |  | 9 | 1260
|  |  |  | Sum | 15608.9548 | W | 71990
https://re.jrc.ec.europa.eu/pvg_tools/en/
|  |  |  | Qtotal | 87598.9548

## Cost
Type | Existing Building (Before) | Improved Building (After) | Unit | Price |  | Total Cost
Annual Thermal Energy | 225973.702 | 39877.6763 | kWh/year | 0.1 | €/kWh | 22597.3702 | 3987.7676
Annual Electricity Load | 21778.9661 | 10705.3085 | kWh/year | 0.25 | €/kWh | 5444.7415 | 2676.3271
HVAC | 2846.9089 | 853.0142 | kWh/year | 0.25 | €/kWh | 711.7272 | 213.2535